## Points
Project Name | Zone Unit
Measurement System | Metric
Model Number | ECY-STAT-Z
Controller Name | Zone
Module Name | IO Module |  | AI | AO | DI | DO
Module Model | STAT 4UI-3DO-2DUO |  | 3 | 1 | 0 | 2
Inputs
PointIndex | PointName | PointDescription | AI | AO | DI | DO | SignalType
HI101 | DischargeTemp | Discharge Temperature Sensor | X |  |  |  | RTD & Thermistors/10K Type II
HI102
HI103
HI104
Outputs
HO101
HO102
HO103
HO104 | Reheat1 | Reheat Stage 1 |  |  |  | X | Digital
HO105 | PerimHeat1 | Perimeter Heat Stage 1 |  |  |  | X | Digital
HO106 | DamperCmd | Damper Command |  | X |  |  | Analog 0 - 10 V
HO107
HO108
BLE Sensor Name | ECY-STAT
BLE Sensor Description | ECY-STAT
Inputs
PointIndex | PointName | PointDescription | AI | AO | DI | DO | SignalType
BRI9011 | ECY-STAT SpaceTemp |  | X |  |  |  | SpaceTemp
BRI9012 | ECY-STAT Humidity |  | X |  |  |  | Humidity

## BACnet Objects
Project Name |  | Zone Unit
Measurement System |  | Metric
Model Number |  | ECY-STAT-Z
Controller Name |  | Zone
Index | Type | Name | Description | Default Value | Format
BV12 | Binary Value | RoomOccupancy | Room Occupancy | Unoccupied | Occupied/Unoccupied
BV15 | Binary Value | DisHtCl_WrmUp | Disable Heat & Cool during Mrng Warm Up & Night Purge | No | Yes/No
BV18 | Binary Value | HotWaterReheat | Hot Water Reheat | No | Yes/No
AV5 | Analog Value | SpaceTemp | Actual Space Temperature |  | degrees-Celsius (°C)
AV6 | Analog Value | DuctInTemp | Duct Inlet Temperature |  | degrees-Celsius (°C)
AV7 | Analog Value | SetPtOffset | SetPoint Offset | 0 Δ °C | delta-degrees-Celsius (Δ °C)
AV13 | Analog Value | EffectSpaceTemp | Effective Space Temperature |  | degrees-Celsius (°C)
AV19 | Analog Value | SpaceHumidity | Space Humitidy |  | percent-relative-humidity (% RH)
AV20 | Analog Value | SensorSetpoint | Space Temperature Sensor Setpoint | 22.5 °C | degrees-Celsius (°C)
AV26 | Analog Value | MinDampSP | Minimum Damper Position Setpoint | 15 % | percent (%)
AV27 | Analog Value | MaxCoolDampSP | Cooling Maximum Damper Position Setpoint | 100 % | percent (%)
AV28 | Analog Value | MinHeatDampSP | Heating Minimum Damper Position Setpoint | 25 % | percent (%)
AV29 | Analog Value | MaxHeatDampSP | Heating Maximum Damper Position Setpoint | 100 % | percent (%)
AV30 | Analog Value | MinDampStbySP | Standby Minimum Damper Position Setpoint | 15 % | percent (%)
AV31 | Analog Value | MinDampUnoccSP | Unoccupied Minimum Damper Position Setpoint | 0 % | percent (%)
AV36 | Analog Value | ActCoolSP | Actual Cooling Setpoint |  | degrees-Celsius (°C)
AV37 | Analog Value | ActHeatSP | Actual Heating Setpoint |  | degrees-Celsius (°C)
AV38 | Analog Value | UnoccCoolSP | Unoccupied Cooling Setpoint | 27 °C | degrees-Celsius (°C)
AV39 | Analog Value | StandbyCoolSP | Standby Cooling Setpoint | 25.5 °C | degrees-Celsius (°C)
AV40 | Analog Value | OccCoolSP | Occupied Cooling Setpoint | 23.5 °C | degrees-Celsius (°C)
AV41 | Analog Value | OccHeatSP | Occupied Heating Setpoint | 19 °C | degrees-Celsius (°C)
AV42 | Analog Value | StandbyHeatSP | Standby Heating Setpoint | 18 °C | degrees-Celsius (°C)
AV43 | Analog Value | UnoccHeatSP | Unoccupied Heating Setpoint | 17 °C | degrees-Celsius (°C)
AV44 | Analog Value | TerminalLoad | Terminal Load | 0 % | percent (%)
AV45 | Analog Value | TerminalLoadF | Terminal Load Factorized | 0 % | percent (%)
AV46 | Analog Value | ChgOverDelay | Change Over Delay (Heat/Cool) | 2 min | minutes (min)
AV47 | Analog Value | BypassTime | Bypass Mode Override Time | 60 min | minutes (min)
AV50 | Analog Value | EffectSP | Effective Space Temperature Setpoint |  | degrees-Celsius (°C)
AV51 | Analog Value | TempErr | Temperature Deviation from Setpoint |  | delta-degrees-Kelvin (Δ K)
AV54 | Analog Value | HoldTime | Motion Sensor Hold Time | 900 s | seconds (s)
AV68 | Analog Value | HeatModeTempErr | Temperature Deviation from Heating Setpoint |  | delta-degrees-Kelvin (Δ K)
AV69 | Analog Value | CoolModeTempErr | Temperature Deviation from Cooling Setpoint |  | delta-degrees-Kelvin (Δ K)
AV71 | Analog Value | TerminalLoadHF | Terminal Load Heat Factor | 100 % | percent (%)
AV72 | Analog Value | TerminalLoadCF | Terminal Load Cool Factor | 100 % | percent (%)
MSV1 | Multi State Value | OccupancyCmd | Occupancy Command | Occupied | Occupied, Unoccupied, Bypass, Standby
MSV2 | Multi State Value | HVACModeCmd | HVAC Mode Command | Auto | Auto, Heat, MrngWrmup, Cool, NightPurge, PreCool, Off
MSV13 | Multi State Value | HeatPriority | Duct vs Perimeter Heat Priority | DuctHeater | DuctHeater, PerimeterHeat, Simultaneous
MSV14 | Multi State Value | HVACModeStatus | HVAC Mode Status | Auto | Auto, Heat, MrngWrmup, Cool, NightPurge, PreCool, Off
MSV15 | Multi State Value | OccupancyStatus | Occupancy Status | Occupied | Occupied, Unoccupied, Bypass, Standby
MSV31 | Multi State Value | EcoVue | EcoVue Actual Status | 4Leaves | 1Leaf, 2Leaves, 3Leaves, 4Leaves